## Replacement Boiler Sizing Calc
Replacement Boiler Sizing Chart
Type of System |  | Steam |  | Forced Hot Water |  |  | Gravity Hot Water
Type of Fuel |  | Oil |  | Natural Gas |  |  | LPG
Brand Name of Present Boiler
Model Number
Boiler Input (BTUH)
Square Feet of Radiation
Output (Heating Capacity - BTUH)
Standing Radiation | [8 empty] | Baseboard Radiation
Room | Sq Ft. Per Section (see Standing Radiation Tab) |  | x | Number of Sections |  | = | Radiation in Sq. Ft. |  | Lineal Feet (Length of Finned Tube Only)
|  |  | x |  |  | = | 0
|  |  | x |  |  | = | 0
|  |  | x |  |  | = | 0
|  |  | x |  |  | = | 0
|  |  | x |  |  | = | 0
|  |  | x |  |  | = | 0
|  |  | x |  |  | = | 0
|  |  | x |  |  | = | 0
|  |  | x |  |  | = | 0
|  |  | x |  |  | = | 0
|  |  | x |  |  | = | 0
|  |  | x |  |  | = | 0
[5 empty] | Total Sq Ft. of Radiation |  | 0 | Total Linear Feet | 0
[5 empty] | Conversion Factor (see below) | x |  | x 600 BTU/Ft. | 600
[5 empty] | Total BTUH Load |  | 0 | Total BTUH Load | 0
Conversion Factors 1 sq. ft. of steam radiation = 240 Net BTUH 1 sq. ft. of forced hot water = 185 Net BTUH at 190ºF

## Standing Radiation
Column Type Radiators
Sq. Ft. Radiation Per Section
Height (Inches) | One Column | Two Column | Three Column | Four Column | Window
13 | --- | --- | --- | --- | 3
16 | --- | --- | --- | --- | 3-3/4
18 | --- | --- | 2-1/4 | 3 | 4-1/4
20 | 1-1/2 | 2 | --- | --- | 5
22 | --- | --- | 3 | 4 | ---
23 | 1-2/3 | 2-1/3 | --- | --- | ---
26 | 2 | 2-2/3 | 3-3/4 | 5 | ---
32 | 2-1/2 | 3-1/3 | 4-1/2 | 6-1/2 | ---
38 | 3 | 4 | 5 | 8 | ---
45 | --- | 5 | 6 | 10 | ---
Tube Type Radiators
Sq. Ft. Radiation Per Section
Height (Inches) | Three Tube | Four Tube | Five Tube | Six Tube | Window Seven Tube
14 | --- | --- | --- | --- | 2-1/2
17 | --- | --- | --- | --- | 3
20 | 1-3/4 | 2-1/4 | 2-2/3 | 3 | 3-2/3
23 | 2 | 2-1/2 | 3 | 3-1/2 | ---
26 | 2-1/3 | 2-3/4 | 3-1/2 | 4 | 4-3/4
32 | 3 | 3-1/2 | 4-1/3 | 5 | ---
38 | 3-1/2 | 4-1/4 | 5 | 6 | ---
Wall Type Radiators
Sq. Ft. Radiation Per Wall Radiator Section
Type of Section | Height (Inches) | Length (Inches) | Thickness (Inches) | Heating Sq. Ft. Radiation
5-A | 13-5/16 | 16-5/8 | 2-7/8 | 5
7-A | 13-5/16 | 21-7/8 | 2-7/8 | 7
7-B | 21-7/8 | 13-3/16 | 3-1/16 | 7
9-A | 18-5/16 | 29-1/16 | 2-7/8 | 9
9-B | 29-1/16 | 18-5/16 | 3-11/16 | 9